**2023 ANNUAL DRINKING WATER QUALITY REPORT**

**PWSID #: 2660014 Tunkhannock Borough Municipal Authority**

Este informe contiene información importante acerca de su agua potable. Haga que alguien lo traduzca para usted, ó hable con alguien que lo entienda. (This report contains important information about your drinking water. Have someone translate it for you or speak with someone who understands it.)

*WATER SYSTEM INFORMATION:*

This report shows our water quality and what it means. If you have any questions about this report or concerning your water utility, please contact Roger Hadsall at (570) 836-3493 . We want you to be informed about your water supply. If you want to learn more, please attend any of our regularly scheduled meetings. They are held the second Tuesday of each month at 6:30 p.m. in the office facility located at 201 W. Tioga St., Tunkhannock PA. Meetings are open to the public. Unvaccinated attendees are asked to wear a mask.

*SOURCE(S) OF WATER:*

Our water sources are:

|  |
| --- |
| Hill Wells 1 and 2, Tunkhannock TownshipSwale Brook Well, Tunkhannock BoroughRavine Well, Tunkhannock TownshipSunnyside Well, Tunkhannock Borough |

*Source Water Assessments* for 3 of our 5 sources were completed in 2005 by the Environmental Resources Research institute of Pennsylvania State University and PA Department of Environmental Protection (Pa. DEP). The Assessments have stated that some of our sources are *potentially* most susceptible to agricultural contaminants, contaminants from major roadways, contaminants from low and high-density development, contamination from underground storage tanks, class 5 underground injection control wells, and contamination from a Resource Conservation and Recovery Act (RCRA) site. Overall, our sources have little to moderate risk of significant contamination. Complete reports for the wells which were assessed were distributed to municipalities, water supplier, local planning agencies and PADEP offices. Copies of the available completed reports are available for review at the Pa. DEP Northeast Regional Office, Records Management Unit at (570) 826-2511.

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by *Cryptosporidium* and other microbial contaminants are available from the *Safe Drinking Water Hotline* (800-426-4791).

*Monitoring Your Water:*

We routinely monitor for contaminants in your drinking water according to federal and state laws. The following tables show the results of our monitoring for the period of January 1 to December 31, 2023. The State allows us to monitor for some contaminants less than once per year because the concentrations of these contaminants do not change frequently. Some of our data is from prior years in accordance with the Safe Drinking Water Act. The date has been noted on the sampling results table.

*DEFINITIONS:*

*Action Level (AL)* - The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

*Maximum Contaminant Level (MCL)* - The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

*Maximum Contaminant Level Goal (MCLG)* - The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

*Maximum Residual Disinfectant Level (MRDL)* - The highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

*Maximum Residual Disinfectant Level Goal (MRDLG)* - The level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

*Minimum Residual Disinfectant Level* *(MinRDL) -* The minimum level of residual disinfectant required at the entry point to the distribution system.

*Treatment Technique (TT) -* A required process intended to reduce the level of a contaminant in drinking water.

*Mrem/year =* millirems per year (a measure of radiation absorbed by the body)

*pCi/L =* picocuries per liter (a measure of radioactivity)

*ppb* = parts per billion, or micrograms per liter (μg/L)*ppm* = parts per million, or milligrams per liter (mg/L)

*ppq* = parts per quadrillion, or picograms per liter

*ppt* = parts per trillion, or nanograms per liter

*DETECTED SAMPLE RESULTS:*

|  |
| --- |
| *Chemical Contaminants* |
| Contaminant | MCL in CCR Units | MCLG | Level Detected | Range of Detections | Units | Sample Date | Violation Y/N | Sources of Contamination |
| Arsenic | 10 | 0 | 7 | 1-7 | ppb | 08/04/21 | N | Erosion of natural deposits; Runoff from orchards; Runoff from glass and electronics production wastes |
| Barium | 2 | 2 | 0.294 | 0.131-0.294 | ppm | 08/04/21 | N | Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural deposits |
| Chlorine\* | MRDL=4 | MRDLG=4 | 1.57 | 1.01-1.57 | ppm | 2023 | N | Water additive used to control microbes |
| Dalapon | 200 | 200 | 2.04 | <1.25-2.04 | ppb | 2023 | N | Runoff from herbicide on rights of way |
| Nitrate | 10 | 10 | 3.04 | <0.25-3.04 | ppm | 08/02/23 | N | Runoff from fertilizer use; Leaching from septic tanks, sewage; Erosion of natural deposits |
| Total Trihalomethanes (TTHMs) | 80 | n/a | 24.1 | 24.1 | ppb | 08/02/23 | N | By-product of drinking water chlorination |
| Haloacetic Acids (HAA5) | 60 | n/a | 12.2 | 12.2 | ppb | 08/02/23 | N | By-product of drinking water chlorination |

\*Distribution system chlorine residual is reported as the highest monthly average and the range of monthly averages.

|  |  |
| --- | --- |
|  | *Entry Point Disinfectant Residual*  |
| Contaminant | Location ID | Minimum DisinfectantResidual | LowestLevel Detected | Range of Detections | Units | Sample Date | Violation Y/N | Sources of Contamination |
| Chlorine | 101 | 0.40 | 1.42 | 1.42-2.20 | ppm | 2023 | N | Water additive used to control microbes. |
| Chlorine | 102 | 0.46 | 0.18 | 0.18-2.20 | ppm | 2023 | N | Water additive used to control microbes. |
| Chlorine | 103 | 0.40 | 0.87 | 0.87-2.18 | ppm | 2023 | N | Water additive used to control microbes. |
| Chlorine | 104 | 0.40 | 0.75 | 0.75-2.20 | ppm | 2023 | N | Water additive used to control microbes. |

|  |  |
| --- | --- |
|  | *Lead and Copper* |
| Contaminant | Action Level (AL) | MCLG | 90th Percentile Value | Units | # of Sites Above AL of Total Sites | Sample Date | Violation Y/N | Sources ofContamination |
| Copper | 1.3 | 1.3 | 0.407 | ppm | 0 | 2022 | N | Corrosion of household plumbing. |

|  |  |
| --- | --- |
|  | *Radiological Contaminants* |
| Contaminant | Site ID | MCL in CCR Units | MCLG | Level Detected | Range of Detect-ions | Units | Sample Date | Violation Y/N | Sources of Contamination |
| Combined Radium | 103 | 5 | 0 | 0.282 | 0.282 | pCi/L | 8/22/18 | N | Erosion of natural deposits |

*The following table shows the unregulated contaminants we detected last year. Unregulated contaminants are those for which EPA has not established drinking water standards. The purpose of unregulated contaminant monitoring is to help EPA determine their occurrence in drinking water and potential need for future regulation.*

|  |  |
| --- | --- |
|  | Unregulated Contaminants – UCMR 5 |
| Contaminant | Location ID | Average Detected Level | Range of Detections | Units | Sample Date |
| Lithium | 101 | 25.3 | 23.1-27.6 | ppb | 2023 |
| Lithium | 102 | 142.5 | 132.0-153.0 | ppb | 2023 |
| Lithium | 103 | 36.9 | 36.3-37.6 | ppb | 2023 |
| Lithium | 104 | 16.2 | 13.7-18.7 | ppb | 2023 |
| perfluorohexanoic acid (PFHxA) | 101 | 4.3 | 4.3-4.4 | ppt | 2023 |
| perfluorooctanesulfonic acid (PFOS) | 101 | 6.1 | 5.6-6.6 | ppt | 2023 |
| perfluorooctanoic acid (PFOA) | 101 | 4.8 | <4.0-4.8 | ppt | 2023 |
| perfluoropentanoic acid (PFPeA) | 101 | 5.3 | 5.0-5.5 | ppt | 2023 |

The fifth Unregulated Contaminant Monitoring Rule (UCMR 5) requires sample collection for 30 chemical contaminants. UCMR 5 will provide new data that will improve the agency’s understanding of the frequency that 29 per- and polyfluoroalkyl substances (PFAS) and lithium are found in the nation’s drinking water systems, and at what levels.

Complete sample results for the UCMR 5 sampling are available at the Authority office.

*EDUCATIONAL INFORMATION:*

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs and wells. As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water include:

* + Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
* Inorganic contaminants, such as salts and metals, which can be naturally occurring or result from urban stormwater run-off, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
* Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
* Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems.
* Radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, EPA and DEP prescribes regulations which limit the amount of certain contaminants in water provided by public water systems. FDA and DEP regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s *Safe Drinking Water Hotline* (800-426-4791).

*Information about Lead*

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Tunkhannock Borough Municipal Authority is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at [*http://www.epa.gov/safewater/lead*](http://www.epa.gov/safewater/lead)*.*

*Information about Arsenic*

While your drinking water meets EPA’s standard for arsenic, it does contain low levels of arsenic. EPA’s standard balances the current understanding of arsenic’s possible health effects against the costs of removing arsenic from drinking water. EPA continues to research the health effects of low levels of arsenic which is a mineral known to cause cancer in humans at high concentrations and is linked to other health effects such as skin damage and circulatory problems.